| FEATURES: Three Phase & Single phase Switchable Equal Power Open Type Gasoline Generator |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | OHV Over Head Valve easy to maintenance |  |  | Circuit Protector Circuit Protector is a device capable of carrying and interrupting both load and fault current up to a certain rating |  |
|  | Oil Level Alarm When the oil level is low that the engine will not start. |  |  | Voltmeter It is a gauge for output voltage of generator set. |  |
|  | AVR AVR is a device often solid state, for controlling the output voltage of a generator |  |  | Choke System When the cold weather, choke system aid to operate the engine. |  |
|  | Wheel Transport System |  |  | Dual Element Air Filter Dual-element air filter that purifies the sucked air from dust and dirt |  |
|  |  |  |  | Switchable Single Phase & Three Phase The possibility of switching between single 220V and three phases 380V |  |

| Generator |  | Engine |  | Size |  |
| --- | --- | --- | --- | --- | --- |
| Standby Power | 10 kVA | Model | QST 460 | Weight | 74 kg |
| Prime Power | 9 kVA | Max. Output Power | 18 hp /13.3 kW | Width | 520 mm |
| Continues Rated Current | 39.15 / 38.88 A | Rotation Speed | 3000 / 3600 r/min | Length | 700 mm |
| Dc Output | 8.3 A / 12v | Cooling System | Air-Cooled | Height | 570 mm |
| Starting System | Electrical Start | Oil Type | 10-30 or 15-40 |  |  |
| Rated Voltage | 220 / 380 V | Fuel Tank Capacity | 33 L |  |  |
| Fuel Type | Gasoline | Bore × Stroke | 92 x 69 mm |  |  |
| Number of Phases | Three / Single Phase Equal Power | Displacement | 0.460 L |  |  |
| Noise Level | 74 Db | Lubrication oil capacity | 1.1 L |  |  |
| Continuous Operating Time | 12 H | Engine Type | 1-Cylinder, 4-Stroke, OHV, Gasoline Engine |  |  |
| Rated Frequency | 60 / 50 Hz |  |  |  |  |
| Power Factor (cosφ) | 1.0 / 0.8 |  |  |  |  |

Continuous Power

The maximum power which a generating set is capable of delivering continuouslywhilst supplying a constant electrical load. Average load can be 100%. The generator must not be overloaded.

Standby Power
The maxpower available during a variable electrical power sequence, under the stated operating conditions, for which a generating set is capable of delivering in the event of a utilitypower outage or under test conditions for up to 200 hrs of operation per year under average of 70%load.Overloading isn’t permissible.

Prime Power

The maximum power which a generating set is capable of delivering continuouslywhilst supplying a variable electrical load. Average load should be 70%. The generator can be overloaded 10% for 1 hour per 12 hrs.